## Lines
|  |  | Substation_1 | Substation_2 |  | Maximum Current Imax (A) | [6 empty] | Dynamic line rating (DLR) |  | Electrical Parameters
NE_name | EIC_Code | TSO | Substation_1 | Substation_2 | Voltage_level(kV) | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Period 6 | Inom(A) | DLRmin(A) | DLRmax(A) | Resistance_R(Ohm) | Resistance_Rd(Ohm/km) | Reactance_X(Ohm) | Reactance_Xd(Ohm/km) | Susceptance_Bd(uS/km) | Susceptance_B(uS) | Length_(km) | Comment
Aschach - Hausruck 203B | 14T-220-0-0203BF | APG | Aschach | Hausruck | 220 | [6 empty] | 800 |  |  | 3.478 | 0.065623 | 19.63 | 0.37038 | 3.2056 | 169.8972 | 53
Aschach - St. Peter 203A | 14T-220-0-0203AH | APG | Aschach | St. Peter | 220 | [6 empty] | 800 |  |  | 4.27 | 0.050713 | 28.5 | 0.33848 | 3.5188 | 296.2836 | 84.2
Bisamberg - Duernrohr 297 | 14T-220-0-002977 | APG | Bisamberg | Duernrohr | 220 | [6 empty] | 2080 |  |  | 1.1 | 0.021526 | 12.7 | 0.24853 | 3.2707 | 167.1327 | 51.1
Bisamberg - Duernrohr 298 | 14T-220-0-002985 | APG | Bisamberg | Duernrohr | 220 | [6 empty] | 2080 |  |  | 1.1 | 0.021526 | 12.7 | 0.24853 | 3.2707 | 167.1327 | 51.1
Bisamberg - Kledering 228B | 14T-220-0-0228BT | APG | Bisamberg | Kledering | 220 | [6 empty] | 1200 |  |  | 2.165 | 0.057733 | 11.71 | 0.31227 | 3.6786 | 137.9473 | 37.5
Bisamberg - Wien Suedost 227 | 14T-220-0-00227S | APG | Bisamberg | Wien Suedost | 220 | [6 empty] | 1200 |  |  | 2.248 | 0.057789 | 12.14 | 0.31208 | 3.6762 | 143.0052 | 38.9
Bisamberg - Ybbsfeld 207 | 14T-220-0-00207Y | APG | Bisamberg | Ybbsfeld | 220 | [6 empty] | 800 |  |  | 8.876 | 0.077452 | 47.31 | 0.41283 | 2.8071 | 321.699 | 114.6
Bisamberg - Ybbsfeld 208 | 14T-220-0-00208W | APG | Bisamberg | Ybbsfeld | 220 | [6 empty] | 800 |  |  | 8.876 | 0.077452 | 47.31 | 0.41283 | 2.8071 | 321.699 | 114.6
Ernsthofen - Hausruck 203C | 14T-220-0-0203CD | APG | Ernsthofen | Hausruck | 220 | [6 empty] | 1000 |  |  | 1.164 | 0.025359 | 13.15 | 0.28649 | 4.0492 | 185.8569 | 45.9
Ernsthofen - Klaus 201B | 14T-220-0-0201BL | APG | Ernsthofen | Klaus | 220 | [6 empty] | 925 |  |  | 3.47 | 0.051484 | 18 | 0.26706 | 1.9043 | 128.35 | 67.4
Ernsthofen - Sattledt 204C | 14T-220-0-0204CA | APG | Ernsthofen | Sattledt | 220 | [6 empty] | 1070 |  |  | 0.869 | 0.025409 | 9.823 | 0.28722 | 4.0537 | 138.638 | 34.2
Ernsthofen - Wallsee 205A | 14T-220-0-0205AB | APG | Ernsthofen | Wallsee | 220 | [6 empty] | 810 |  |  | 1.79 | 0.079911 | 9.27 | 0.41384 | 2.8008 | 62.7376 | 22.4
Ernsthofen - Weissenbach 202 | 14T-220-0-002027 | APG | Ernsthofen | Weissenbach | 220 | [6 empty] | 925 |  |  | 6.67 | 0.079028 | 34.49 | 0.40865 | 2.8445 | 240.08 | 84.4
Ernsthofen - Ybbsfeld 206 | 14T-221-0-00206Q | APG | Ernsthofen | Ybbsfeld | 220 | [6 empty] | 810 |  |  | 3.44 | 0.078005 | 18.24 | 0.41361 | 2.8032 | 123.6215 | 44.1
Feistritz - Obersielach 268 | 14T-220-0-00268E | APG | Feistritz | Obersielach | 220 | [6 empty] | 2080 |  |  | 1.238 | 0.0259 | 14.2 | 0.29707 | 3.8882 | 185.8566 | 47.8
Feistritz - Villach Süd 266C | 14T-220-0-0266CH | APG | Feistritz | Villach Süd | 220 | [6 empty] | 2080 |  |  | 0.761 | 0.018426 | 8.727 | 0.21131 | 2.7651 | 114.2 | 41.3
Greuth - Lienz 266A | 14T-220-0-0266AL | APG | Greuth | Lienz | 220 | [6 empty] | 2080 |  |  | 2.111 | 0.025902 | 24.23 | 0.2973 | 3.8933 | 317.2999 | 81.5
Greuth - Villach Süd 266B |  | APG | Greuth | Villach Süd | 220 | [6 empty] | 2080 |  |  | 0.308 | 0.0037791 | 3.535 | 0.043374 | 0.56785 | 46.28 | 81.5
Hausruck - Sattledt 204B | 14T-220-0-0204BC | APG | Hausruck | Sattledt | 220 | [6 empty] | 1000 |  |  | 0.295 | 0.025214 | 3.33 | 0.28462 | 4.0384 | 47.2495 | 11.7
Hessenberg - Obersielach 286 | 14T-220-0-00286C | APG | Hessenberg | Obersielach | 220 | [6 empty] | 800 |  |  | 8.379 | 0.084296 | 41.2 | 0.41449 | 2.8104 | 279.35 | 99.4
Hessenberg - Ternitz 225A | 14T-220-0-0225A3 | APG | Hessenberg | Ternitz | 220 | [6 empty] | 750 |  |  | 8.03 | 0.084349 | 39.5 | 0.41492 | 2.8106 | 267.5694 | 95.2
Hessenberg - Ternitz 226A | 14T-220-0-0226A0 | APG | Hessenberg | Ternitz | 220 | [6 empty] | 750 |  |  | 8.03 | 0.084349 | 39.5 | 0.41492 | 2.8106 | 267.5694 | 95.2
Hessenberg - Weissenbach 223 | 14T-221-0-00223Q | APG | Hessenberg | Weissenbach | 220 | [6 empty] | 800 |  |  | 5.99 | 0.084248 | 29.5 | 0.41491 | 2.8106 | 199.8367 | 71.1
Hessenberg - Weissenbach 224 | 14T-220-0-00224Y | APG | Hessenberg | Weissenbach | 220 | [6 empty] | 800 |  |  | 5.99 | 0.084248 | 29.5 | 0.41491 | 2.8106 | 199.8367 | 71.1
Hessenberg - Zeltweg 287 | 14T-220-0-00287A | APG | Hessenberg | Zeltweg | 220 | [6 empty] | 800 |  |  | 3.634 | 0.084316 | 17.87 | 0.41462 | 2.8107 | 121.14 | 43.1
Jochenstein - Schaerding 237 | 14T-220-0-00237P | APG | Jochenstein | Schaerding | 220 | [6 empty] | 720 |  |  | 2.08 | 0.084898 | 9.6 | 0.39184 | 2.9249 | 71.6597 | 24.5
Jochenstein - Schaerding 238 | 14T-220-0-00238N | APG | Jochenstein | Schaerding | 220 | [6 empty] | 720 |  |  | 2.08 | 0.084898 | 9.6 | 0.39184 | 2.9249 | 71.6597 | 24.5
Kledering - Wien Suedost 228A | 14T-220-0-0228AV | APG | Kledering | Wien Suedost | 220 | [6 empty] | 1200 |  |  | 0.12 | 0.057143 | 0.65 | 0.30952 | 3.5799 | 7.5178 | 2.1
Lienz - Villach Süd 267A | 14T-220-0-0267AI | APG | Lienz | Villach Süd | 220 | [6 empty] | 2000 |  |  | 2.414 | 0.021945 | 27.71 | 0.25191 | 3.2991 | 362.8999 | 110
Mayrhofen - Zell am Ziller 219 | 14T-220-0-00219R | APG | Mayrhofen | Zell am Ziller | 220 | [6 empty] | 2000 |  |  | 0.25 | 0.027174 | 2.8 | 0.30435 | 4.0192 | 36.9765 | 9.2
Mayrhofen - Zell am Ziller 220 | 14T-220-0-002205 | APG | Mayrhofen | Zell am Ziller | 220 | [6 empty] | 2000 |  |  | 0.25 | 0.027174 | 2.8 | 0.30435 | 4.0192 | 36.9765 | 9.2
Neusiedl - Wien Suedost 246A | 14T-220-0-0246AT | APG | Neusiedl | Wien Suedost | 220 | [6 empty] | 800 |  |  | 3.69 | 0.081278 | 18.9 | 0.4163 | 2.7818 | 126.292 | 45.4
Obersielach - Rosegg 267C | 14T-220-0-0267CE | APG | Obersielach | Rosegg | 220 | [6 empty] | 2000 |  |  | 1.532 | 0.025922 | 17.59 | 0.29763 | 3.8951 | 230.2 | 59.1
Obersielach - Zeltweg 285 | 14T-220-0-00285E | APG | Obersielach | Zeltweg | 220 | [6 empty] | 800 |  |  | 5.841 | 0.084286 | 28.73 | 0.41457 | 2.8107 | 194.78 | 69.3
Phyrn - Weissenbach 201A | 14T-220-0-0201AN | APG | Phyrn | Weissenbach | 220 | [6 empty] | 925 |  |  | 1.395 | 0.080172 | 7.143 | 0.41052 | 2.8006 | 48.73 | 17.4
Rosegg - Villach Süd 267B | 14T-220-0-0267BG | APG | Rosegg | Villach Süd | 220 | [6 empty] | 2000 |  |  | 0.429 | 0.0072466 | 4.92 | 0.083108 | 1.0878 | 64.4 | 59.2
Salzburg Elixhausen - Tauern 231A | 14T-220-0-0231AB | APG | Salzburg Elixhausen | Tauern | 220 | [6 empty] | 800 |  |  | 8.364 | 0.084914 | 40.69 | 0.4131 | 2.7981 | 275.6119 | 98.5
Salzburg Elixhausen - Tauern 232A | 14T-220-0-0232A8 | APG | Salzburg Elixhausen | Tauern | 220 | [6 empty] | 800 |  |  | 8.364 | 0.084914 | 40.69 | 0.4131 | 2.7981 | 275.6119 | 98.5
St. Peter - Schaerding 235 | 14T-220-0-00235T | APG | St. Peter | Schaerding | 220 | [6 empty] | 800 |  |  | 3.12 | 0.085246 | 14.4 | 0.39344 | 2.9253 | 107.0654 | 36.6
St. Peter - Schaerding 236 | 14T-220-0-00236R | APG | St. Peter | Schaerding | 220 | [6 empty] | 800 |  |  | 3.12 | 0.085246 | 14.4 | 0.39344 | 2.9253 | 107.0654 | 36.6
Tauern - Weissenbach 221 | 14T-220-0-002213 | APG | Tauern | Weissenbach | 220 | [6 empty] | 800 |  |  | 10.42 | 0.084304 | 51.2 | 0.41424 | 2.8112 | 347.4601 | 123.6
Tauern - Weissenbach 222 | 14T-220-0-002221 | APG | Tauern | Weissenbach | 220 | [6 empty] | 800 |  |  | 10.42 | 0.084304 | 51.2 | 0.41424 | 2.8112 | 347.4601 | 123.6
Ternitz - Wien Suedost 225B | 14T-220-0-0225B1 | APG | Ternitz | Wien Suedost | 220 | [6 empty] | 960 |  |  | 5.075 | 0.085294 | 24.59 | 0.41328 | 2.791 | 166.065 | 59.5
Ternitz - Wien Suedost 226B | 14T-220-0-0226BZ | APG | Ternitz | Wien Suedost | 220 | [6 empty] | 960 |  |  | 5.075 | 0.085294 | 24.59 | 0.41328 | 2.791 | 166.065 | 59.5
Wallsee - Ybbsfeld 205B | 14T-220-0-0205B9 | APG | Wallsee | Ybbsfeld | 220 | [6 empty] | 810 |  |  | 2.33 | 0.078451 | 12.26 | 0.41279 | 2.8063 | 83.3465 | 29.7
Westtirol - Zell am Ziller 275 | 14T-220-0-00275H | APG | Westtirol | Zell am Ziller | 220 | [6 empty] | 2100 |  |  | 2.66 | 0.0257 | 30.8 | 0.29758 | 3.8853 | 402.1238 | 103.5
Westtirol - Zell am Ziller 276 | 14T-220-0-00276F | APG | Westtirol | Zell am Ziller | 220 | [6 empty] | 2100 |  |  | 2.66 | 0.0257 | 30.8 | 0.29758 | 3.8853 | 402.1238 | 103.5
Bisamberg - Duernrohr 436A | 14T-380-0-0436AJ | APG | Bisamberg | Duernrohr | 380 | [6 empty] | 2300 |  |  | 1.11 | 0.021722 | 15.52 | 0.30372 | 3.7791 | 193.1136 | 51.1
Bisamberg - Duernrohr 444A | 14T-380-0-0444AL | APG | Bisamberg | Duernrohr | 380 | [6 empty] | 2300 |  |  | 1.109 | 0.021703 | 15.52 | 0.30372 | 3.7791 | 193.1136 | 51.1
Bisamberg - Sarasdorf 435C | 14T-380-0-0435CI | APG | Bisamberg | Sarasdorf | 380 | [6 empty] | 2300 |  |  | 1.078 | 0.021734 | 15.05 | 0.30343 | 3.7921 | 188.0871 | 49.6
Bisamberg - Sarasdorf 443C | 14T-380-0-0443CK | APG | Bisamberg | Sarasdorf | 380 | [6 empty] | 2300 |  |  | 1.077 | 0.021714 | 15.05 | 0.30343 | 3.7921 | 188.0871 | 49.6
Duernrohr - Etzersdorf 434B | 14T-380-0-0434BN | APG | Duernrohr | Etzersdorf | 380 | [6 empty] | 2300 |  |  | 0.3 | 0.021583 | 4.4 | 0.31655 | 3.6727 | 51.0509 | 13.9
Duernrohr - Kronstorf 433 | 14T-380-0-00433L | APG | Duernrohr | Kronstorf | 380 | [6 empty] | 2300 |  |  | 2.56 | 0.02164 | 37.2 | 0.31445 | 3.6754 | 434.7963 | 118.3
Duernrohr - Wien Suedost 435A | 14T-380-0-0435AM | APG | Duernrohr | Wien Suedost | 380 | [6 empty] | 2300 |  |  | 2.75 | 0.021654 | 38.62 | 0.30409 | 3.7823 | 480.3494 | 127
Duernrohr - Wien Suedost 443A | 14T-380-0-0443AO | APG | Duernrohr | Wien Suedost | 380 | [6 empty] | 2300 |  |  | 2.75 | 0.021654 | 38.62 | 0.30409 | 3.7823 | 480.3494 | 127
Etzersdorf - Kronstorf 434A | 14T-380-0-0434AP | APG | Etzersdorf | Kronstorf | 380 | [6 empty] | 2300 |  |  | 2.26 | 3.2286 | 32.82 | 46.8857 | 547.9834 | 383.5884 | 0.7
Kainachtal - Obersielach 471 | 14T-380-0-00471D | APG | Kainachtal | Obersielach | 380 | [6 empty] | 2300 |  |  | 1.56 | 0.021667 | 22.88 | 0.31778 | 3.7123 | 267.2867 | 72
Kainachtal - Obersielach 472 | 14T-380-0-00472B | APG | Kainachtal | Obersielach | 380 | [6 empty] | 2300 |  |  | 1.56 | 0.021667 | 22.88 | 0.31778 | 3.7123 | 267.2867 | 72
Kronstorf - St. Peter 431 | 14T-380-0-00431P | APG | Kronstorf | St. Peter | 380 | [6 empty] | 2300 |  |  | 2.411 | 0.021662 | 34.98 | 0.31429 | 3.6807 | 409.6636 | 111.3
Kronstorf - St. Peter 432 | 14T-380-0-00432N | APG | Kronstorf | St. Peter | 380 | [6 empty] | 2300 |  |  | 2.411 | 0.021662 | 34.98 | 0.31429 | 3.6807 | 409.6636 | 111.3
Lienz - Tauern 451 | 14T-380-0-00451J | APG | Lienz | Tauern | 380 | [6 empty] | 2180 |  |  | 1.847 | 0.021729 | 26.76 | 0.31482 | 3.6631 | 311.3631 | 85
Lienz - Tauern 452 | 14T-380-0-00452H | APG | Lienz | Tauern | 380 | [6 empty] | 2180 |  |  | 1.85 | 0.021765 | 26.8 | 0.31529 | 3.6661 | 311.6145 | 85
Oststeiermark - Dreibein Mellach 475SR | 14T-380-0-0475MJ | APG | Oststeiermark | Dreibein Mellach | 380 | [6 empty] | 2400 |  |  | 0.53 | 0.018662 | 9.04 | 0.31831 | 5.5166 | 156.6712 | 28.4
Oststeiermark - Wien Suedost 477 | 14T-380-0-004771 | APG | Oststeiermark | Wien Suedost | 380 | [6 empty] | 2400 |  |  | 2.51 | 0.015212 | 42.47 | 0.25739 | 4.4553 | 735.1326 | 165
Sarasdorf - Wien Suedost 435D | 14T-380-0-0435DG | APG | Sarasdorf | Wien Suedost | 380 | [6 empty] | 2300 |  |  | 0.56 | 0.021293 | 8.05 | 0.30608 | 3.7604 | 98.8973 | 26.3
Sarasdorf - Wien Suedost 443D | 14T-380-0-0443DI | APG | Sarasdorf | Wien Suedost | 380 | [6 empty] | 2300 |  |  | 0.56 | 0.021293 | 8.05 | 0.30608 | 3.7711 | 99.18 | 26.3
Sarasdorf - Zurndorf 439A | 14T-380-0-0439AA | APG | Sarasdorf | Zurndorf | 380 | [6 empty] | 2300 |  |  | 0.63 | 0.021951 | 8.778 | 0.30585 | 3.7633 | 108.0079 | 28.7
Sarasdorf - Zurndorf 440A | 14T-380-0-0440AX | APG | Sarasdorf | Zurndorf | 380 | [6 empty] | 2300 |  |  | 0.63 | 0.021951 | 8.778 | 0.30585 | 3.7633 | 108.0079 | 28.7
Schwarzenbach - Tauern 417B | 14T-380-0-0417BM | APG | Schwarzenbach | Tauern | 380 | [6 empty] | 2400 |  |  | 0.142 | 0.011452 | 3.742 | 0.30177 | 3.8358 | 47.5637 | 12.4
Schwarzenbach - Zell am Ziller 417A | 14T-380-0-0417AO | APG | Schwarzenbach | Zell am Ziller | 380 | [6 empty] | 2400 |  |  | 0.651 | 0.011481 | 16.93 | 0.29859 | 3.8702 | 219.4402 | 56.7
St. Peter - Salzburg Elixhausen 455 | 14T-220-0-00455F | APG | St. Peter | Salzburg Elixhausen | 380 | [6 empty] | 2400 |  |  | 0.64 | 0.014066 | 11.72 | 0.25758 | 4.4707 | 203.4181 | 45.5
St. Peter - Salzburg Elixhausen 456 | 14T-220-0-00456D | APG | St. Peter | Salzburg Elixhausen | 380 | [6 empty] | 2400 |  |  | 0.64 | 0.014066 | 11.72 | 0.25758 | 4.4707 | 203.4181 | 45.5
Suedburgenland - Dreibein Mellach 476SU | 14T-380-0-0476MG | APG | Suedburgenland | Dreibein Mellach | 380 | [6 empty] | 2400 |  |  | 1.413 | 0.022938 | 23.73 | 0.38523 | 6.6759 | 411.2344 | 61.6
Suedburgenland - Wien Suedost 478 | 14T-381-0-00478Q | APG | Suedburgenland | Wien Suedost | 380 | [6 empty] | 2400 |  |  | 1.633 | 0.015148 | 27.76 | 0.25751 | 4.4559 | 480.3494 | 107.8
Tauern - Zell am Ziller 418 | 14T-380-0-00418H | APG | Tauern | Zell am Ziller | 380 | [6 empty] | 2400 |  |  | 0.79 | 0.011433 | 20.67 | 0.29913 | 3.864 | 267.0039 | 69.1

## Tielines
|  |  | Substation_1 | Substation_2 |  | Maximum Current Imax (A) | [6 empty] | Dynamic line rating (DLR) |  | Electrical Parameters | [5 empty] | TSO Share until border
NE_name | EIC_Code | TSO | Full_name | Full_name | Voltage_level(kV) | Period 1 | Period 2 | Period 3 | Period 4 | Period 5 | Period 6 | Fixed | DLRmin(A) | DLRmax(A) | Resistance_R(Ω) | Resistance_Rd(Ohm/km) | Reactance_X(Ω) | Reactance_Xd(Ohm/km) | Susceptance_Bd(μS/km) | Susceptance_B(μS) | Length_(km) | Comment
Bisamberg - Sokolnice 243 | 10T-AT-CZ-000010 | APG | Bisamberg | Sokolnice | 220 | [6 empty] | 655 |  |  | 5.25 | 0.068093 | 25.6 | 0.33204 | 2.2248 | 171.5309 | 77.1
Bisamberg - Sokolnice 244 | 10T-AT-CZ-00002Z | APG | Bisamberg | Sokolnice | 220 | [6 empty] | 655 |  |  | 5.25 | 0.068093 | 25.6 | 0.33204 | 2.2248 | 171.5309 | 77.1
Duernrohr - Slavetice 437 | 10T-AT-CZ-00003X | APG | Duernrohr | Slavetice | 380 | [6 empty] | 2250 |  |  | 1.0335 | 0.019376 | 14.265 | 0.26744 | 3.5129 | 187.3802 | 53.34
Duernrohr - Slavetice 438 | 10T-AT-CZ-00004V | APG | Duernrohr | Slavetice | 380 | [6 empty] | 2250 |  |  | 1.0335 | 0.019376 | 14.265 | 0.26744 | 3.5129 | 187.3802 | 53.34
Kainachtal - Maribor 473 | 10T-AT-SI-00001T | APG | Kainachtal | Maribor | 380 | [6 empty] | 1920 |  |  | 0.725 | 0.021513 | 9.05 | 0.26855 | 3.1453 | 105.9973 | 33.7
Kainachtal - Maribor 474 | 10T-AT-SI-00002R | APG | Kainachtal | Maribor | 380 | [6 empty] | 1920 |  |  | 0.725 | 0.021513 | 9.05 | 0.26855 | 3.1453 | 105.9973 | 33.7
Lienz - Soverzene 261 | 10T-AT-IT-00001V | APG | Lienz | Soverzene | 220 | [6 empty] | 704 |  |  | 3.74 | 0.11131 | 19.155 | 0.57009 | 3.6932 | 124.0929 | 33.6
Meiningen - Buers 406A | 10T-AT-DE-000231 | APG | Meiningen | Buers | 220 | [6 empty] | 2040 |  |  | 0.37 | 0.012803 | 4.49 | 0.15536 | 1.8099 | 52.3075 | 28.9
Meiningen - Ruethi 407 | 10T-AT-CH-00003T | APG | Meiningen | Ruethi | 220 | [6 empty] | 2400 |  |  | 0.06 | 0.025 | 0.8 | 0.33333 | 3.5083 | 8.42 | 2.4
Meiningen - Ruethi 408 | 10T-AT-CH-00004R | APG | Meiningen | Ruethi | 220 | [6 empty] | 2400 |  |  | 0.05 | 0.020833 | 0.76 | 0.31667 | 3.6167 | 8.68 | 2.4
Neusiedl - Gyoer 246B | 10T-AT-HU-00001W | APG | Neusiedl | Gyoer | 220 | [6 empty] | 600 |  |  | 3.325 | 0.14648 | 17.105 | 0.75352 | 5.0106 | 113.7413 | 22.7
Obersielach - Podlog 247 | 10T-AT-SI-00003P | APG | Obersielach | Podlog | 220 | [6 empty] | 920 |  |  | 1.99 | 0.10153 | 13.44 | 0.68571 | 4.7469 | 93.0383 | 19.6
St.Peter - Altheim 233/230 | 10T-AT-DE-00001B | APG | St.Peter | Altheim | 220 | [6 empty] | 1077 |  |  | 0.147 | 0.077368 | 0.757 | 0.39842 | 2.9084 | 5.526 | 1.9
St.Peter - Pirach 256 | 10T-AT-DE-000029 | APG | St.Peter | Pirach | 220 | [6 empty] | 1350 |  |  | 0.134 | 0.070526 | 0.698 | 0.36737 | 4.9284 | 9.364 | 1.9
St.Peter - Pleinting 258 | 10T-AT-DE-000037 | APG | St.Peter | Pleinting | 220 | [6 empty] | 1350 |  |  | 0.134 | 0.070526 | 0.698 | 0.36737 | 4.9284 | 9.364 | 1.9
St.Peter - Simbach 234/230 | 10T-AT-DE-000045 | APG | St.Peter | Simbach | 220 | [6 empty] | 1077 |  |  | 0.147 | 0.077368 | 0.757 | 0.39842 | 2.9084 | 5.526 | 1.9
Walgauwerk - Buers 405A | 10T-AT-DE-10024U | APG | Walgauwerk | Buers | 220 | [6 empty] | 2040 |  |  | 0.185 | 0.0053623 | 2.24 | 0.064928 | 0.75125 | 25.9181 | 34.5
Westtirol - Buers 421 | 10T-AT-DE-000061 | APG | Westtirol | Buers | 220 | [6 empty] | 2140 |  |  | 1 | 0.01087 | 14.35 | 0.15598 | 1.8491 | 170.1172 | 92
Westtirol - Buers 422 | 10T-AT-DE-000053 | APG | Westtirol | Buers | 380 | [6 empty] | 2300 |  |  | 0.99 | 0.010761 | 14.25 | 0.15489 | 1.8337 | 168.7035 | 92
Westtirol - Kempten 411 | 10T1001C--00037V | APG | Westtirol | Kempten | 220 | [6 empty] | 1795 |  |  | 1.527 | 0.032489 | 12.54 | 0.26681 | 4.4838 | 210.738 | 47
Westtirol - Leupolz 412 | 10T-AT-DE-10007U | APG | Westtirol | Leupolz | 380 | [6 empty] | 2392 |  |  | 1.33 | 0.028298 | 10.65 | 0.2266 | 3.7866 | 177.9712 | 47
Westtirol - Pradella 427 | 10T-AT-CH-00002V | APG | Westtirol | Pradella | 380 | [6 empty] | 2240 |  |  | 0.835 | 0.01401 | 11.4 | 0.19128 | 2.2626 | 134.8528 | 59.6
Westtirol - Pradella 428 | 10T-AT-CH-00001X | APG | Westtirol | Pradella | 380 | [6 empty] | 2240 |  |  | 0.835 | 0.01401 | 11.4 | 0.19128 | 2.2626 | 134.8528 | 59.6
Wien Suedost - Gyoer 245 | 10T-AT-HU-00002U | APG | Wien Suedost | Gyoer | 220 | [6 empty] | 600 |  |  | 4.992 | 0.079113 | 25.665 | 0.40674 | 2.706 | 170.7455 | 63.1
Zurndorf - Gyoer 439B | 10T-AT-HU-00003S | APG | Zurndorf | Gyoer | 380 | [6 empty] | 2000 |  |  | 0.19 | 0.021348 | 2.79 | 0.31348 | 3.657 | 32.5469 | 8.9
Zurndorf - Szombathely 440B | 10T-AT-HU-00004Q | APG | Zurndorf | Szombathely | 380 | [6 empty] | 2000 |  |  | 0.19 | 0.021348 | 2.79 | 0.31348 | 3.657 | 32.5469 | 8.9

## Transformers
Location |  |  | Maximum Current Imax (A) primary |  |  | Voltage_level(kV) |  | Electrical Parameters (primary) at neutral tap |  |  |  | Phase Shifting Properties
Full Name | EIC_Code | TSO | Min | Max | Fixed | Primary | Secondary | Resistance_R(Ω) | Reactance_X(Ω) | Susceptance_B (µS) | Conductance_G (µS) | Taps used for RAO | Theta θ (°) | Symmetrical/Asymmetrical | Phase Regulation δu (%) | Angle Regulation δu (%) | Comment
Duernrohr DURHU41 | 14T-38220-DR0410 | APG |  |  | 1556 | 220 | 380 | 0.2196 | 15.786 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
Duernrohr DURHU42 | 14T-38220-DR042Z | APG |  |  | 1556 | 220 | 380 | 0.2196 | 15.786 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
Ernsthofen EHRHU41 | 14T-38220-EH0425 | APG |  |  | 1556 | 220 | 380 | 0.2196 | 15.873 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
Ernsthofen EHRHU42 | 14T-38220-EH0417 | APG |  |  | 1556 | 220 | 380 | 0.2196 | 15.786 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
Ernsthofen EHPST | 14T-22220-EHPST5 | APG |  |  | 1493 | 220 | 220 | 0.1223 | 12.827 | 63.1514 | 1.6833 | -6; +6 | 90 | SYMM |  | 2.252 | PST
Lienz LIRHU41 | 14T-38220-LI041Y | APG |  |  | 1554 | 220 | 380 | 0.2196 | 15.433 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
Lienz LIRHU42 | 14T-38220-LI042W | APG |  |  | 1554 | 220 | 380 | 0.2196 | 15.433 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
Lienz LIPST | 14T-22220-LIPSTW | APG |  |  | 746 | 220 | 220 | 0.2937 | 23.591 | 4.3939 | 1.7895 |  | 90 | SYMM |  | 3.616 | PST; coordinated in Italy North
Obersielach OSRHU41 | 14T-38220-OS0413 | APG |  |  | 1556 | 220 | 380 | 0.2196 | 15.433 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
Obersielach OSRHU43 | 14T-RHU43-OS---K | APG |  |  | 1531 | 220 | 380 | 0.1773 | 15.609 | -10.0555 | 2.6427 |  | 60 | ASYM |  | 1.253
Obersielach OSRHU42 | 14T-38220-OS0421 | APG |  |  | 1556 | 220 | 380 | 0.2196 | 15.433 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
St. Peter SPRHU41 | 14T-38220-SP041V | APG |  |  | 1427 | 220 | 380 | 0.1942 | 15.099 | -6.7194 | 2.7958 |  | -60 | ASYM |  | 1.253
St. Peter SPRHU42 | 14T-38220-SP042T | APG |  |  | 1427 | 220 | 380 | 0.1942 | 15.099 | -6.7194 | 2.7958 |  | -60 | ASYM |  | 1.253
St. Peter SPRHU43 |  | APG |  |  | 1427 | 220 | 380 | 0.1942 | 15.099 | -6.7194 | 2.7958 |  | -60 | ASYM |  | 1.253
Tauern TARHU41 | 14T-38220-TA041Q | APG |  |  | 1554 | 220 | 380 | 0.1925 | 15.432 | -12.6401 | 5.0472 |  | 60 | ASYM |  | 1.253
Tauern TARHU42 | 14T-38220-TA042O | APG |  |  | 1554 | 220 | 380 | 0.1925 | 15.432 | -12.6401 | 5.0472 |  | 60 | ASYM |  | 1.253
Tauern TAPST | 14T-22220-TAPSTO | APG |  |  | 1493 | 220 | 220 | 0.1223 | 12.827 | 63.1514 | 1.6833 | -6; +6 | 90 | SYMM |  | 2.252 | PST
Ternitz TEPST | 14T-22220-TEPST4 | APG |  |  | 1493 | 220 | 220 | 0.1223 | 12.827 | 63.1514 | 1.6833 | -6; +6 | 90 | SYMM |  | 2.252 | PST
Westtirol WTRHU41 | 14T-38220-WT041O | APG |  |  | 1443 | 380 | 220 | 0.2987 | 21.601 | -6.6615 | 1.7 |  | 59.99 | ASYM |  | 1.388
Wien Suedost SORHU41 | 14T-38221-SO041S | APG |  |  | 1556 | 220 | 380 | 0.2196 | 15.786 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
Wien Suedost SORHU43 | 14T-38220-SO042Y | APG |  |  | 1556 | 220 | 380 | 0.2196 | 15.786 | -16.0268 | 5.7088 |  | 60 | ASYM |  | 1.253
Zell am Ziller ZZRHU41 | 14T-38220-ZZ041D | APG |  |  | 1732 | 380 | 220 | 0.2257 | 19.736 | -22.4514 | 1.0437 |  | 59.95 | ASYM |  | 1.25
Zell am Ziller ZZRHU42 | 14T-38220-ZZ042B | APG |  |  | 1732 | 380 | 220 | 0.2257 | 19.736 | -22.4514 | 1.0437 |  | 59.95 | ASYM |  | 1.25

## Remedial Actions
Location
Name of RA | TSO | Description
EHPST | APG | Change of tap position of phase shifting transformer (220/220) in 220kV substation Ernsthofen
TAPST | APG | Change of tap position of phase shifting transformer (220/220) in 220kV substation Tauern
TEPST | APG | Change of tap position of phase shifting transformer (220/220) in 220kV substation Ternitz
SPCPL1 | APG | Opening of busbar coupler in 380kV substation St. Peter (Normal operation: one-node operation)